Products for Indoor Air Quality and Control

CARNES COMPANY 448 South Main St., Verona, WI 53593

Phone 608-845-6411, Fax 608-845-6470, carnes@carnes.com

WRITTEN SPECIFICATION GUIDE

MODEL(S): ADCC/ADCD

DUAL  DUCT TERMINAL UNITS

DIVISION 23

NOTICE:

Carnes Company authorizes the use of this document, which is strictly informative in nature, for aiding in the creation of written specifications.  Carnes Company assumes no liability for any results from the use of this document regardless if it is modified or not.

- GENERAL

  - SUMMARY

(NOTE: Edit items as needed for job requirements)

    - Section Includes: Terminal Units

      - Dual Duct

  - RELATED SECTIONS

(NOTE: Edit items as needed for job requirements)

      - 01 00 00 General Requirements

  - REFERENCES

(NOTE: Edit items as needed for job requirements)

    - AHRI 880-2008

    - AHRI 885-2008

    - NFPA 90

    - UL 181

  - SUBMITTALS

(NOTE: Edit items as needed for job requirements)

    - General: Refer to Division 01 for submittal procedures

    - Product Data: Provide data for each unit including:

      - Catalog data

      - Dimensional drawings

      - Performance data for criteria listed on the schedule

    - Provide manufacturer's installation, operations, and maintenance manual (IOM)

  - QUALITY ASSURANCE

(NOTE: Edit items as needed for job requirements)

    - Qualifications: Manufacturer shall have a minimum of five years manufacturing the type of products specified in this section

    - Performance shall be AHRI certified and bear the AHRI label.

  - DELIVERY, STORAGE, AND HANDLING

(NOTE: Edit items as needed for job requirements)

    - Packaging: Units shall be shipped in protective packaging

    - Storage: Store materials as recommended by manufacturer

    - Handling: Handle units in accordance with the manufacturer’s instructions

  - WARRANTY

(NOTE: Edit items as needed for job requirements)

    - Manufacturer's Warranty: Equipment shall be free from defects in material and workmanship for a period of one year from the ship date

  - MAINTENANCE

(NOTE: Edit items as needed for job requirements)

    - Refer to Manufacturer's Installation, Operation and Maintenance Manual (IOM), to find maintenance procedures

- PRODUCTS

  - MANUFACTURER

    - Carnes

  - DUAL DUCT AIR TERMINAL UNITS

(NOTE: Edit items as needed for job requirements)

    - General:

      - Furnish and install Carnes variable air volume terminal units of size, capacity, and performance as shown on the plans

      - Label each unit clearly identifying maximum and minimum CFM, tag/mark number, unit model number, and manufacturer’s order number

      - Include factory applied calibration chart/ label to each unit

    - Construction:

      - Units shall have a round inlets with square/rectangle discharge slip and drive connection

      - Valve assembly shall consist of gasket material sandwiched between two pieces of galvanized steel.  Incorporate a mechanical stop to prevent overstroking

      - Valve assemblies shall operate independent of each other

      - Damper shaft shall be 3/8” rotating in oil impregnated sintered bronze bearings.  Nylon bearings shall not be acceptable.  Shaft shall be clearly marked indicating the damper position without the use of stickers or other removable markings.

      - Include factory supplied and mounted controls enclosure

      - Include factory supplied and mounted primary airflow sensor

      - Casing shall be constructed to allow for internal mixing/blending. Units with two single duct units mounted side-by-side shall not be acceptable

      - Units designed for constant volume applications shall include an airflow sensor factory installed near the casing discharge

    - Casing:

      - Minimum 22 gauge galvanized steel

    - Casing Lining:

      - Dual density matte faced fiberglass:

        - Internally line casing with < 1/2” > OR < 1” > thick 1.5 pound dual density matte faced fiberglass complying to UL 181 and NFPA 90

        - Insulation R-Value shall be a minimum of 2.0

OR

      - Dual density foil faced fiberglass:

        - Internally line casing with < 1/2” > OR < 1” > thick 1.5 pound dual density foil faced fiberglass complying to UL 181 and NFPA 90

        - Insulation R-Value shall be a minimum of 2.0

OR

      - Closed cell fiber free liner:

        - Internally line casing with ½” closed cell fiber free foam liner complying to UL 181 and NFPA 90

        - Insulation R-Value shall be a minimum of 2.0

        - Cover cut edges with foil tape

    - Primary Airflow Sensor:

      - Sensor shall be “H” shaped multi-point center averaging type with a minimum of three averaging chambers.  Sensors with only one averaging chamber and/or single axis sensors shall not be acceptable.

      - A minimum of four pressure sensing points shall be available yielding an output factor of at least 2.0

    - Controls:

      - Controls shall be supplied by ATC and shipped to VAV manufacturer for factory mounting

      - Controls shall be supplied and field mounted by ATC

      - Include factory supplied and mounted pressure independent analog controls with wall thermostat

      - Include factory supplied and mounted pneumatic controls.  Pneumatic thermostat shall be supplied by installing contractor

    - Transformer:

      - Include factory supplied and mounted 24 volt transformer

      - 24 volt transformer shall be supplied and mounted by the ATC

    - Discharge Sound Attenuators:

      - Supply factory supplied discharge sound attenuator for field mounting

      - Connection method shall be slip and drive

      - Line attenuator with the same insulation as the terminal unit

      - Attenuator shall be a minimum of 24” in length

- EXECUTION

  - MANUFACTURER'S INSTRUCTIONS

    - Refer to Installation, Operation, and Maintenance Manual (IOM)

  - PREPARATION

    - Refer to Installation, Operation, and Maintenance Manual (IOM)

  - INSTALLATION

    - Refer to Installation, Operation, and Maintenance Manual (IOM)

- END OF SECTION