Products for Indoor Air Quality and Control

CARNES COMPANY 448 South Main St., Verona, WI 53593

Phone 608-845-6411, Fax 608-845-6470, carnes@carnes.com

WRITTEN SPECIFICATION GUIDE

MODEL(S): LRBK/LNBK

SIDEWALL PROPELLER FANS

DIVISION 23

NOTICE:

Carnes Company authorizes the use of this document, which is strictly informative in nature, for aiding in the creation of written specifications.  Carnes Company assumes no liability for any results from the use of this document regardless if it is modified or not.

- GENERAL

  - SUMMARY

(NOTE: Edit items as needed for job requirements)

    - Section Includes: HVAC Power Ventilators

      - Sidewall Propeller Fans

  - RELATED SECTIONS

(NOTE: Edit items as needed for job requirements)

      - 01 00 00 General Requirements

  - REFERENCES

(NOTE: Edit items as needed for job requirements)

    - Air Movement and Control Association Inc. (AMCA):

      - 99 - Standards Handbook

      - 200 - Publication, Air Systems

      - 201-90 - Publication, Fans and Systems

      - 203-90 - Publication, Field Performance Measurement of Fan Systems

      - 211-05 - Publication, Certified Ratings Program – Product Rating Manual for Fan Air Performance

      - 300-96 - Standard Reverberant Room Method for Sound Testing of Fans

      - 311-05 - Publication Certified Ratings Program – Product Rating Manual for Fan Sound Performance

    - Air Movement and Control Association Inc. (AMCA), American National Standards Institute (ANSI):

      - 210-99 - Standard Laboratory Methods of Testing Fans for Aerodynamic Performance Rating

    - American Society of Heating, Refrigerating and Air Conditioning Engineers, Inc. (ASHRAE):

      - Chapter 18 - 1992 HVAC System and Equipment handbook, Fans

      - Chapter 45 - 2003 Handbook, HVAC Applications

    - National Fire Protection Association (NFPA)

      - 70 - National Electrical Code

    - Underwriters Laboratories (UL):

      - 705 - Standard Power Ventilators

  - SUBMITTALS

(NOTE: Edit items as needed for job requirements)

    - General: Refer to Division 01 for submittal procedures

    - Product Data: Provide data for each unit including:

      - Catalog data

      - Dimensional drawings

      - Fan curves at the specified capacity

      - Sound power levels at the specified capacity

      - Motor characteristics including voltage, RPM, and type

    - Installation, Operation, and Maintenance Manual (IOM): Provide manufacturer's installation, operations, and maintenance manual

  - QUALITY ASSURANCE

(NOTE: Edit items as needed for job requirements)

    - Qualifications: Manufacturer shall have a minimum of five years manufacturing the type of products specified in this section

    - AMCA Certification: Conform to AMCA standard 211 and 311. Fans shall be certified to bear the AMCA label for sound and air performance

    - NEMA Compliance: Motors and electrical accessories shall comply with the National Electrical Manufacturers Association (NEMA) standards

    - UL Standard: Units shall comply with the UL 705 standard

    - Fan RPM shall be factory set and run tested

  - DELIVERY, STORAGE, AND HANDLING

(NOTE: Edit items as needed for job requirements)

    - Packaging: Units shall be shipped in protective crates

    - Storage: Store materials as recommended by manufacturer

    - Handling: Handle units in accordance with the manufacturer’s instructions

  - WARRANTY

(NOTE: Edit items as needed for job requirements)

    - Manufacturer's Warranty: Equipment shall be free from defects in material and workmanship for a period of one year from the ship date.

  - MAINTENANCE

(NOTE: Edit items as needed for job requirements)

    - Refer to Manufacturer's Installation, Operation and Maintenance Manual (IOM), to find maintenance procedures

- PRODUCTS

  - MANUFACTURER

    - Carnes

  - SIDEWALL MOUNTED PROPELLER FANS-BELT DRIVE

(NOTE: Edit items as needed for job requirements)

    - General Description:

      - Units shall be either supply or exhaust as indicated on the schedule

      - Sidewall mounted

      - Belt driven

    - Wheel:

      - Material type: Cast aluminum blades and hubs

      - Securely attached to fan shaft by square key and set screw

      - Statically and dynamically balanced

    - Motors:

      - Motor enclosures: [Open driproof] [Totally enclosed fan cooled] [Explosion resistant] [High efficiency] [Two speed] (NOTE: Combine descriptions as needed)

    - Shafts and Bearings:

      - Fan Shaft shall be ground and polished steel with an anti corrosive coating

      - Bearing shall be cast iron pillow block with factory installed grease fittings

      - Bearings shall have a minimum average life in excess of 200,000 hours.

    - Motor Plate:

      - Motor mounting plate shall be heavy gauge steel with “J” bolt adjustments to ensure consistent and proper drive belt tension

      - Finish: [Mill] [Baked Enamel] [Epoxy] [Acid Resistant Coating (ARC)] [Air Dry Enamel] [Air Dry Heresite]

    - Drive Frame:

      - Drive frame shall be welded and bolted structural steel angle frame

      - Finish: [Mill] [Baked Enamel] [Epoxy] [Acid Resistant Coating (ARC)] [Air Dry Enamel] [Air Dry Heresite]

    - Disconnect Switches:

      - NEMA rated: [1] [3R] [4] [4X] [7&9] [12]

    - Drive assembly:

      - Cast iron construction sized for a minimum of 150% of the installed motor HP and keyed to both the motor and fan shaft

      - Motor sheave shall be adjustable for final system balancing

      - Sheaves on motor HP’s of 3 and up shall be two-grooved

      - Belts shall be oil resistant, static free, and rated for a minimum of 25,000 hours average life

    - Accessories:

      - Dampers:

        - Type: [Gravity] [Motorized] Motorized Voltage[115] [230]

        - Galvanized flanged frame with pre-punched mounting holes

      - Combination Louver/Backdraft Dampers:

        - Material: Extruded aluminum

        - Louver blades shall be positioned on a 39 degree angle and 4.25” centers

        - Damper blades shall move independent of each other

        - Birdscreen: Factory install ¾” x .051” flattened aluminum birdscreen in removable frame.

        - Finish: [Mill] [Baked Enamel] [Kynar] [Clear Anodized [Dark Bronze] [Prime Coat]

      - Combination Drainable Blade Louver

        - Material: Extruded aluminum

        - Louver blades shall be positioned on a 37 degree angle and 3.0” centers

        - Actuator shall be [120 volt] [24 volt] 2 position with a spring return

        - Birdscreen: Factory install ¾” x .051” flattened aluminum birdscreen in removable frame.

        - Finish: [Mill] [Baked Enamel] [Kynar] [Clear Anodized [Dark Bronze] [Prime Coat]

      - Damper Guard:

        - Guard material: Steel

        - Shall meet OSHA  requirements and completely enclose the damper and exterior wall opening

      - Supply Grille:

        - Constructed of heavy duty welded galvanized steel frame with hinges to allow access to the fan, bearings, and drives

        - Blades shall be double deflection aluminum airfoil type

        - Designed to mount to a wall box on the motor side of the fan

      - Finishes:

        - Types: [Mill]  [Baked Enamel] [Epoxy] [Acid Resistant Coating (ARC)] [Air Dry Enamel] [Air Dry Heresite]

      - Wall Box:

        - Mounting arrangement: [Flush Interior] [Flush Exterior] [Flush Interior Reverse] [Flush Exterior Reverse]

        - Constructed of [Steel] [Aluminum]

        - Wall box shall include OSHA approved motor guard

      - Wall Collar:

        - Constructed of [Steel] [Aluminum]

      - Motor Side Guard:

        - Guard type: [Basket Style] [OSHA Style]

        - Constructed of galvanized steel

        - Coat with baked electrocoat enamel

      - Weatherhood:

        - Material type: [Galvanized Steel] [Aluminum]

        - Turndown Angle: 45 degrees

        - Screen: [Birdscreen] [OSHA Guard]

        - Finishes: [Mill] [Baked Enamel] [Acid Resistant Coating (ARC)] [Air Dry Enamel] [Air Dry Heresite]

- EXECUTION

  - MANUFACTURER'S INSTRUCTIONS

    - Compliance: Refer to Installation, Operation, and Maintenance Manual (IOM)

  - PREPARATION

    - Refer to Installation, Operation, and Maintenance Manual (IOM)

  - INSTALLATION

    - Refer to Installation, Operation, and Maintenance Manual (IOM)

  - SYSTEM STARTUP

    - Refer to Installation, Operation, and Maintenance Manual (IOM)

  - ADJUSTING

    - Refer to Installation, Operation, and Maintenance Manual (IOM)

  - CLEANING

    - Refer to Installation, Operation, and Maintenance Manual (IOM)

  - PROTECTION

    - Refer to Installation, Operation, and Maintenance Manual (IOM)

- END OF SECTION