Products for Indoor Air Quality and Control

CARNES COMPANY 448 South Main St., Verona, WI 53593

Phone 608-845-6411, Fax 608-845-6470, carnes@carnes.com

WRITTEN SPECIFICATION GUIDE

MODEL(S): LYDK/LZDK

SIDEWALL PROPELLER FANS

DIVISION 23

NOTICE:

Carnes Company authorizes the use of this document, which is strictly informative in nature, for aiding in the creation of written specifications.  Carnes Company assumes no liability for any results from the use of this document regardless if it is modified or not.

- GENERAL

  - SUMMARY

(NOTE: Edit items as needed for job requirements)

    - Section Includes: HVAC Power Ventilators

      - Sidewall Propeller Fans

  - RELATED SECTIONS

(NOTE: Edit items as needed for job requirements)

      - 01 00 00 General Requirements

  - REFERENCES

(NOTE: Edit items as needed for job requirements)

    - Air Movement and Control Association Inc. (AMCA):

      - 99 - Standards Handbook

      - 200 - Publication, Air Systems

      - 201-90 - Publication, Fans and Systems

      - 203-90 - Publication, Field Performance Measurement of Fan Systems

      - 211-05 - Publication, Certified Ratings Program – Product Rating Manual for Fan Air Performance

      - 300-96 - Standard Reverberant Room Method for Sound Testing of Fans

      - 311-05 - Publication Certified Ratings Program – Product Rating Manual for Fan Sound Performance

    - Air Movement and Control Association Inc. (AMCA), American National Standards Institute (ANSI):

      - 210-99 - Standard Laboratory Methods of Testing Fans for Aerodynamic Performance Rating

    - American Society of Heating, Refrigerating and Air Conditioning Engineers, Inc. (ASHRAE):

      - Chapter 18 - 1992 HVAC System and Equipment handbook, Fans

      - Chapter 45 - 2003 Handbook, HVAC Applications

    - National Fire Protection Association (NFPA)

      - 70 - National Electrical Code

    - Underwriters Laboratories (UL):

      - 705 - Standard Power Ventilators

  - SUBMITTALS

(NOTE: Edit items as needed for job requirements)

    - General: Refer to Division 01 for submittal procedures

    - Product Data: Provide data for each unit including:

      - Catalog data

      - Dimensional drawings

      - Fan curves at the specified capacity

      - Sound power levels at the specified capacity

      - Motor characteristics including voltage, RPM, and type

    - Installation, Operation, and Maintenance Manual (IOM): Provide manufacturer's installation, operations, and maintenance manual

  - QUALITY ASSURANCE

(NOTE: Edit items as needed for job requirements)

    - Qualifications: Manufacturer shall have a minimum of five years manufacturing the type of products specified in this section

    - AMCA Certification: Conform to AMCA standard 211 and 311. Fans shall be certified to bear the AMCA label for sound and air performance

    - NEMA Compliance: Motors and electrical accessories shall comply with the National Electrical Manufacturers Association (NEMA) standards

    - UL Standard: Units shall comply with the UL 705 standard

    - Fan shall be factory run tested

  - DELIVERY, STORAGE, AND HANDLING

(NOTE: Edit items as needed for job requirements)

    - Packaging: Units shall be shipped in protective container

    - Storage: Store materials as recommended by manufacturer

    - Handling: Handle units in accordance with the manufacturer’s instructions

  - WARRANTY

(NOTE: Edit items as needed for job requirements)

    - Manufacturer's Warranty: Equipment shall be free from defects in material and workmanship for a period of one year from the ship date.

  - MAINTENANCE

(NOTE: Edit items as needed for job requirements)

    - Refer to Manufacturer's Installation, Operation and Maintenance Manual (IOM), to find maintenance procedures

- PRODUCTS

  - MANUFACTURER

    - Carnes

  - SIDEWALL MOUNTED PROPELLER FANS-DIRECT DRIVE

(NOTE: Edit items as needed for job requirements)

    - General Description:

      - Units shall be either supply or exhaust as indicated on the schedule

      - Sidewall mounted

      - Direct driven

    - Wheel:

      - Material type: Die formed aluminum blades with steel hubs

      - Securely attached to fan shaft by set screws

      - Statically and dynamically balanced

    - Motors:

      - Motor type: [Open driproof PSC ] [ECM]

      - Motor shall be factory wired to a factory mounted wiring/conduit box

      - Motor shall be mounted to fan panel with neoprene vibration mounts

    - Fan Panel:

      - Fan panel shall be a single piece of 16 gauge [steel] [aluminum] with pre-punched mounting holes, formed flanges, and a deep spun venturi

      - Finish: [baked electrocoat enamel] [Acid Resistant Coating (ARC)] [Air Dry Heresite]

    - Disconnect Switches:

      - NEMA rated: [1] [3R]

    - Accessories:

      - Shutter:

        - Type: [Gravity] [Motorized]

        - Motorized voltage [115 volt] [230 volt] [24 volt] [460 volt] [575 volt]

        - Aluminum flanged frame

      - Combination Louver/Backdraft Dampers:

        - Material: Extruded aluminum

        - Louver blades shall be positioned on a 39 degree angle and 4.25” centers

        - Damper blades shall move independent of each other

        - Birdscreen: Factory install ¾” x .051” flattened aluminum birdscreen in removable frame.

        - Finish: [Mill] [Baked Enamel] [Kynar] [Clear Anodized [Dark Bronze] [Prime Coat]

      - Combination Drainable Blade Louver

        - Material: Extruded aluminum

        - Louver blades shall be positioned on a 37 degree angle and 3.0” centers

        - Actuator shall be [120 volt] [24 volt] 2 position with a spring return

        - Birdscreen: Factory install ¾” x .051” flattened aluminum birdscreen in removable frame.

        - Finish: [Mill] [Baked Enamel] [Kynar] [Clear Anodized [Dark Bronze] [Prime Coat]

      - Propeller Guard:

        - Guard material: Steel

        - Guard type: OSHA Style mounted to fan panel with neoprene vibration mounts

        - Constructed of welded steel

        - Finish: [baked electrocoat enamel] [Acid Resistant Coating (ARC)] [Air Dry Heresite]

      - Finishes:

        - Types: [Mill]  [Baked Enamel] [Acid Resistant Coating (ARC)] [Air Dry Heresite]

      - Wall Box:

        - Mounting arrangement: Flush Exterior

        - Constructed of [Steel] [Aluminum] with pre-punched mounting holes

        - Finish: [baked electrocoat enamel] [Acid Resistant Coating (ARC)] [Air Dry Heresite]

      - Wall Collar:

        - Mounting arrangement: Flush Exterior

        - Constructed of [Steel] [Aluminum] with pre-punched mounting holes

        - Finish: [baked electrocoat enamel] [Acid Resistant Coating (ARC)] [Air Dry Heresite]

      - Motor Side Guard:

        - Guard type: OSHA Style mounted to fan panel with neoprene vibration mounts

        - Constructed of welded steel

        - Finish: [baked electrocoat enamel] [Acid Resistant Coating (ARC)] [Air Dry Heresite]

      - Weatherhood:

        - Material type: [Galvanized Steel] [Aluminum]

        - Turndown Angle: 45 degrees

        - Screen: ½” x .042” birdscreen

        - Finishes: Finish: [baked electrocoat enamel] [Acid Resistant Coating (ARC)] [Air Dry Heresite]

      - Speed Controller (PSC):

        - Factory supplied speed controller to control capacity from full motor RPM to approximately 50%

        - Ship loose for field installation and wiring

      - Speed Controller (VCU controller for ECM):

        - Factory supplied and mounted Visual Control Unit (VCU) to allow for manual adjustment of fan motor

        - Controller shall have a 4 digit LED readout displaying motor RPM and flow index

        - Include factory supplied and mounted 24 volt transformer to power the controller

        - Fan adjustment must be made using a screwdriver

      - Speed Controller (ACU controller for ECM):

        - Factory supplied and mounted Automatic Control Unit (ACU) to allow for remote control of unit using a 0-10 volt signal (by BMS)

        - Controller shall have a LED light indicating flow index

        - Include factory supplied and mounted 24 volt transformer to power the controller

      - Mounting Angles:

        - Include factory supplied mounting angles cut to length to provide a convenient method of attaching wall box to wall

        - Ship loose for field drilling and installation

      - Birdscreen:

        - Include factory supplied ½” x .041” birdscreen

        - Ship loose for field installation

- EXECUTION

  - MANUFACTURER'S INSTRUCTIONS

    - Compliance: Refer to Installation, Operation, and Maintenance Manual (IOM)

  - PREPARATION

    - Refer to Installation, Operation, and Maintenance Manual (IOM)

  - INSTALLATION

    - Refer to Installation, Operation, and Maintenance Manual (IOM)

  - SYSTEM STARTUP

    - Refer to Installation, Operation, and Maintenance Manual (IOM)

  - ADJUSTING

    - Refer to Installation, Operation, and Maintenance Manual (IOM)

  - CLEANING

    - Refer to Installation, Operation, and Maintenance Manual (IOM)

  - PROTECTION

    - Refer to Installation, Operation, and Maintenance Manual (IOM)

- END OF SECTION